This standard operating procedure (SOP) documents procedures to protect employees and prevent combustible materials from exposure to fire, sparks, hot metal, or any other source of ignition whenever hot work is performed outside of a designated safe hot work area. Definitions, responsibilities, hot work requirements, and hot work in confined spaces are discussed below. This SOP also addresses Occupational Safety and Health Administration (OSHA) requirements specified in Title 29 of the Code of Federal Regulations (CFR) 1910.252 for fire prevention and protection during welding, cutting, and brazing, and follows NFPA 51B – Fire Prevention During Welding, Cutting and Other Hot Work.

1.0 DEFINITIONS

Designated Safe Hot Work Area:  An area that has been designed and constructed specifically for performing open-flame or spark-producing work and is maintained free of combustible materials (i.e., maintenance shops can be designated safe hot work areas) and has been certified by an Issuer of Permit.

- The Designated Safe Hot Work Area(s) for Department Name:  (clearly define areas in your department that you deem safe areas not requiring a hot work permit. Identify areas with sign – see appendix A)

- Outside the building at least 40’ from structure or special hazard, not including the roof.

These areas should be inspected prior to each hot work operation to ensure they are free of combustible materials.

Fire watch: At least one individual dedicated solely to the look out and control of stray fires.  See responsibilities in next section.

Hot Work: Work using an open-flame or spark-producing apparatus including, but not limited to welding, cutting, burning, grinding, and related heat-producing operations that could ignite combustible materials or flammable atmospheres. Hot work excludes food preparation operations and use of Bunsen burners in labs (covered in NFPA 45- Standard on Fire Protection for Laboratories Using Chemicals).

Prohibited Areas: Cutting or welding shall not be permitted in the following situations:

- In areas not authorized by management.

- In sprinklered buildings while such protection is impaired.

- In the presence of explosive atmospheres (mixtures of flammable gases, vapors, liquids, or dusts with air), or explosive atmospheres that may develop inside un-cleaned or improperly prepared tanks or equipment which have previously contained such materials, or that may develop in areas with an accumulation of combustible dusts.

- In areas near the storage of large quantities of exposed, readily ignitable materials such as bulk sulfur, baled paper, or cotton.

2.0 RESPONSIBILITIES

University Safety & Assurances (US&A)

US&A is responsible for the umbrella Program consisting of the UWM Hot Work SOP Template, providing initial Hot Work training and annual fire extinguisher training, professional expertise, and annual program review.  US&A may also be called upon, on an emergency basis, to verify permit conditions if a Department Head/Manger and/or Supervisor is unavailable.

Department Heads/Managers

The Department head is responsible for:

- Creating and maintaining a Hot Work SOP specific to their work environment (s)

- Assuring all new employees receive initial training

- Assuring all employees performing fire watch duties receive annual fire extinguisher training

- Identifying and designating qualified Permit Issuers for their departments

Issuer of Permit

The issuer of the permit shall be a qualified, designated individual that is trained with regard to the UWM Hot Work Permit program and fire procedures. The issuer shall issue the permit after conducting a site inspection and prior to hot work beginning.  The issuer will close the permit after conducting a site inspection 30 minutes after completion of the hot work.  Designated personnel shall have the adequate skills to manage the program in their areas.  The following personnel may be designated an issuer of a permit (areas listed in parentheses):

- Department personnel (laboratories, shops, studios, or other academic units)

- Facility Services (work being performed on UWM facilities or grounds by Facility Services personnel or contractors)

- UWM Housing Facilities Assistant Director, B&G Superintendent or B&G Supervisor (work being performed in the UWM Housing buildings)

Supervisor

Supervisors and/or their designees are responsible for:

- Ensuring that employees performing hot work are trained on this SOP and hot work requirements, operation of the hot work equipment, and fire safety and emergency procedures.

- Ensuring that contractor personnel meet requirements detailed in this SOP if performing hot work.

- Ensuring that a hot work permit is obtained from an Issuer of Permit (see above).

Hot work shall not begin until the supervisor can ensure and document the following:

- People and combustible materials will not be exposed to fire, sparks, or any other source of ignition.

- Emergency response procedures are in place.

- The work area is safe.

Fire Watch

The fire watch shall:

- Attend all hot work performed in circumstances where a fire might develop (see below)

- Ensure that the appropriate extinguishing equipment is readily available and be trained in its use

  - The type of hot work procedures performed shall determine the equipment required. At a minimum, an ABC extinguisher shall be provided.  US&A can be consulted for assistance with fire extinguisher selection.

  - Personnel should know the capacity of the fire extinguishing equipment available and not try to extinguish a fire beyond the equipment’s capacity.

- Be trained on emergency fire procedures in the event of a fire

  - In the event of a fire, the fire watch shall sound the fire alarm.

  - See fire procedures at: http://uwm.edu/safety-health/fire/

  - US&A can be consulted for assistance with fire procedures and extinguisher training.

- Remain in a location that allows immediate communication with the individual(s) performing hot work (operator)

- Order that all hot work cease should a fire be discovered

- Remain in the work area a minimum of 30 minutes after the work is completed to ensure the risk of fire from hot work has passed

- Contact the issuer of the permit to close out the hot work permit

Circumstances where a fire might develop are when one or more of the following exist:

- An appreciable amount of combustible material that can be easily ignited (including material such as the building structure or other materials) is within 35 feet of the hot work area

- Wall or floor openings within a 35-foot-radius of the hot work area that expose combustible materials in adjacent areas.  Openings include concealed spaces in walls or floors.

- Combustible materials likely to be ignited by conduction or radiation near the other side of hot work areas near the metal partitions, walls, ceilings, or roofs

Operator

The hot work operator shall:

- Be qualified and trained to properly operate the hot work equipment

- Perform hot work ONLY after a hot work permit has been obtained or after inspecting a designated safe hot work area for combustible materials and removing them.

- Cease all hot work

  - If the above circumstances are present or arise during operation where a fire might develop.

  - Should a fire occur.

  - Upon notification from the fire watch to cease operation.

- Be trained on emergency fire procedures in the event of a fire

  - In the event of a fire, the operator shall sound the fire alarm.

  - See fire procedures at:  http://uwm.edu/safety-health/fire/

  - US&A can be consulted for assistance with fire procedures and extinguisher training.

Contractors

Contractors may use their own hot work permit procedures if they meet or exceed the requirements of the UWM hot work program.  UWM personnel hosting the contractor must be qualified as an issuer of a permit under the UWM program and review the work being done by the contractor to assure it meets standard.

3.0 HOT WORK REQUIREMENTS

The following minimum requirements apply at locations where hot work will be performed:

- A hot work permit shall be completed to authorize hot work performed outside of designated safe hot work areas. Hot work may not begin until a permit has been obtained.

The UWM Hot Work Permit is suitable for most hot work. (see appendix B)

- Combustible materials, including ordinary combustible solids (wood, paper, cardboard, insulation, trash, etc.), and flammable and combustible liquids should be relocated at least 35 feet from the hot work area. If relocation is impractical, combustibles shall be protected with flameproof covers or shielded with metal or flameproof curtains.

- Measures should be taken so as to not inadvertently set off the fire alarm system.

  - Methods to prevent accidental tripping of the system shall be verified with or conducted by Facility Services (229-4742).

  - UWM Police (229-4627) and affected departments shall be notified of fire alarms being disabled.

  - Contact Facility Services to place alarms back into service after hot work is completed.  Notify UWM Police and departments of status.

- Lower areas should be roped off when hot work is performed overhead. Warning signs must then be posted to prevent combustible materials and personnel from entering the lower areas.

- Barriers should be placed around and under hot work areas to confine sparks unless this action is physically impossible.

- Open drains leading to underground systems that may contain flammable or combustible materials should be protected by the following:

  - The atmosphere should be tested for flammable vapors before a permit is issued and

  - The open drain should be covered with a fire blanket or similar protective shield to prevent the entry of sparks, even if a safe atmosphere currently exists.

4.0 HOT WORK IN CONFINED SPACES

When performing hot work in confined spaces, employees shall comply with a Confined Space Entry Program. In addition, employees shall do the following:

- Keep all gas cylinders and welding machines outside of confined spaces (this may not apply to heating/chilling tunnel activities if gas hoses cannot reach the work area).

- Positively isolate the gas supply outside the confined space when torches are not in use for a substantial period of time (such as during a lunch break); when practical, employees shall also remove torches and hoses from confined spaces.

- De-energize electrode holders by electrically disconnecting the power supply when arc welding is to be suspended for an appreciable amount of time or the welder has occasion to leave work.

- Use insulating mats or similar insulating equipment to protect welders using alternating current equipment over 50 volts from electrical contact with conductive materials.

- Ensure that available ventilation in the confined space meets the ventilation requirements set forth in 29 CFR 1910.252(c) (Welding, Cutting, and Brazing- General Requirements).

- Monitoring shall be performed in the confined space area before and during hot work.

  - The permit issuer should specify on the hot work permit the concentrations of vapors and gases in areas, as applicable.

  - Hot work should not be performed if the concentration of flammable gases or vapors exceeds 10 percent of the LEL.

  - If flammable vapors or gases are present, but their levels do not exceed 10 percent of the lower explosive limit (LEL), hot work should not be started until the person approving the permit:

    - Knows the source of the flammable gases or vapors, and

    - Determines that their concentration will not increase while the hot work is in progress.

5.0 RECORDKEEPING

Hot Work Permits

All hot work permits shall be returned to University Safety & Assurances for their record retention. Records of hot work permits shall be maintained for one calendar year. Hot work permits on file should be reviewed for program improvement or modification purposes prior to disposal.

Training

Training that shall be conducted in conjunction with this Hot Work Permit Program includes:

- The provisions of this Hot Work Permit Program

- Fire safety and extinguisher use

- Training for the type of hot work equipment in use

- Confined space entry, if applicable

Copies of records of all program-related training should be maintained in the department personnel files. Copies of training records should be sent to University Safety & Assurances.

Revision Record:

| Date | Comment | Reviewer/Editor |
| --- | --- | --- |

DESIGNATED HOT

WORK AREA

INSPECT THE AREA BEFORE EACH USE FOR

COMBUSTIBLE OR FLAMMABLE MATERIALS AND REMOVE

UW-Milwaukee Hot Work Permit

Hot work is any operation that generates heat, sparks or an open flame. This work includes, but is not necessarily limited to welding, cutting, grinding, soldering, torch- applied roofing, heat gun use, and similar activities and excludes food preparation operations. Fire watchers shall be required whenever welding or cutting is performed in locations where other than a minor fire might develop. Contractors must employ suitably trained personnel who have an awareness of the magnitude of the risks involved and must use only approved apparatuses such as torches, manifolds, and regulators or pressure-reducing valves. This work must comply with 29CFR 1910.252 and NFPA 51B.

BEFORE INITIATING HOT WORK, DETERMINE IF THERE IS A SAFER WAY TO COMPLETE THE WORK.

Date:       		Location (Building, Room):

Hot Work Operator:        			Signature:_______________________

Type of Hot Work:  Soldering   Welding  Cutting  Roofing  Other

THIS PERMIT IS GOOD FOR:   One Day (Max.)      Hours

Hot Work Precautions Check List: Complete prior to any hot work beginning in an area not designated for hot work. Check each box where the statement is true. If any statements are not true, then hot work should not begin until that issue has been safely resolved.

Required Safety Precautions

Fire suppression sprinklers or fire extinguishers are available and operable.

Hot work equipment is operable and in good condition per manufacturer’s specifications.

If smoke/ fire detectors are in the immediate hot work area, they need to be temporarily disabled until the hot work is complete.  Notify Facility Services at 229-4742 to disable the detector.  Notify UWM Police at 229-4627 and affected departments of alarm being disabled.

Building occupants have been protected or isolated from the hot work area.

Drums, barrels, tanks, or enclosed areas have been cleaned, de-pressurized, and purged of flammables and toxics.  All tank feeds are closed and the tank is vented.

Piping should be removed from service, isolated, and vented.

Confined Spaces monitored. Gas concentrations: O2      CO      LEL      H2S

Requirements within 35 feet:

Area within 35 feet of the work area has been swept to remove any combustible debris.

Flammable and ignitable materials (solid, liquid, or gas) and debris have been moved at least 35 feet from the hot work area or covered and protected with fire resistant materials.

Compressed gas cylinders or stored fuel have been removed from the hot work area or have been protected from the hot work.

Cracks or holes in floors, walls, and ceilings (including ductwork) are covered or plugged.

Combustible floors or materials covered with fire-resistive material.

Ducts or other conveyance equipment covered or shut down.

Work on walls or Ceilings

Construction is noncombustible and has no combustible covering or insulation.

Areas adjacent to walls being worked on are checked for combustibles and any combustibles are either removed or protected.

Fire Watch

A fire watch is needed for all hot work activities unless the hot work area has no fire hazards or combustible exposures.

Fire Watch required during Hot Work and a minimum of 30 minutes following completion of work?  Yes  No  Name:

Fire Watch is trained on fire extinguishing equipment and is familiar with the procedures for sounding an alarm in the event of a fire. The Fire Watch will watch for fires in the exposed areas and is responsible for extinguishing spot fires and communicating alarms immediately.

Fire extinguishing equipment readily available.

When work is completed, the fire watch shall have:

Inspected work area, and any potentially affected surrounding areas for fire, fire damage, or potential for fire.

Contacted Facility Services to reactivate smoke/ fire detectors that were disabled because of the hot work.  Notify UWM Police and affected departments.

I verify that the above location has been examined and the necessary precautions have been taken to prevent the outbreak of fire due to Hot Work.

Issuer of Permit- Name: ___________________________	Date:

Signature: ___________________________   	Time Issued:

Closer of Permit- Name: ___________________________	Date:

Signature:  ___________________________   	Time Closed:

Fire Watch Signature: _____________________________

This Permit is valid only for the day issued.

Supervisors shall return completed permit to:

University Safety & Assurances

Engelmann Hall 270

P.O. Box 413, Milwaukee, WI 53201-0413

The information below must be posted in the Hot Work Area:

WARNING!

HOT WORK IN PROGRESS

WATCH FOR FIRE!

**Emergency Numbers**

In case of FIRE, call UWM Police:

Campus phone: 9-911 or Cell phone: (414)229-9911

Facility Services: 229-4742

University Safety & Assurances: 229-6339

HOT WORK DECISION TREE

|  |  |  |  |  | YES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | NO |  |  |  |  |  |  |  |
|  |  |  |  |  | YES |  |  |  |  |  |
|  |  |  | NO |  |  |  |  |  |  |  |
|  |  |  |  |  | YES |  |  |  |  |  |
|  |  |  | NO |  |  |  |  |  |  |  |
|  |  |  |  |  | YES |  |  |  |  |  |
|  |  |  | NO |  |  |  |  |  |  |  |

# Text boxes

# NOTICE